## Night Walk List
NIGHT WALK CHECK LIST |  |  |  |  | Date:
Start Time:
Current Outdoor Air Temp:
End Time:
Organization
Building Name
WHAT TO BRING
Keys to access all intended locations | Powder puff bottle for checking drafts
Pen & paper | IR temperature gun and Thermal imaging camera
Printed floor plans | Multitool and 13-1 screwdriver
Printed HVAC equipment ID & location | PPE - hands, eye, hearing
High powered flashlight | Cell phone for pictures
USEFUL TO KNOW AHEAD OF TIME
HVAC equipment scheduling and what's expected to be running and not | Night Purge setpoint that may turn equipment On
Exhaust fans allowed to operate afterhours | Time clocks and their location
Night Low Limit setpoint that may turn equipment On | Parking lot photocells and their location
HVAC - LOOK, LISTEN & FEEL |  |  | Location |  | Notes
Standing near exterior door, is building in excessive negative or positive pressure? Use powder Puff. Ask yourself why and document for later follow up?
Document any fan systems operating and for later follow up
If boiler running, does current outdoor temperature conditions warrant operation and to what associated equipment?
If boiler is off, are associated pumps needlessly running?
Listen for mechanical air-conditioning running and to what equipment. Is outdoor air temperature ideal for free-cooling?
If chiller running, do current temperature conditions warrant operation and to what associated equipment?
If chiller is off, are associated pumps and cooling towers needlessly running?
If other mechanical air-conditioning running, do current temperature conditions warrant operation?
Look for open or partially open economizer OSA dampers when HVAC scheduled off.
Look for open or partially open economizer OSA dampers when HVAC turned on to meet Low Limit conditions
Listen for Fan Powered Boxes running when no need for heating (random sample diffusers with IR Gun)
Operational cause and effect issues (why something cycles on/off, modulates open/shut, varies in speed or flow, etc.)
Air movement, extreme temperature fluctuations, and humidity levels
Vibrations, humming, rattling, and other mechanical noises coming from HVAC, lighting, etc.
Condensation dripping from equipment or piping? This indicates mechanical cooling is running
Air diffusers blocked by furniture or homemade deflectors
Water spots, standing water, or dripping water
Odors (mold, overheating electrical equipment, chemicals, etc)
Interior Lighting | Location |  |  | Notes
What is the primary type of lighting control? E.g., wall switch, Occ Sensor, Automated Panel
Any common areas overlit?
Opportunity in common area or hallway to branchout to multiple switches?
Is dedicated egress lighting in common/hallway areas overlit and opportunity to remove?
Any occupancy sensors not turning Off after timeout period?
Lighting control panel performing “Sweeps” and any zones still lit?
Exterior Lighting | Location |  |  | Notes
What is the primary type of lighting control? E.g., photocell, Time Clock, Automated Panel
If time clock, check that current time and day is correct
If time clock, review daily sunrise/sunset settings are close to actual
If photocell, are any wallpacks or parking lot lighting still ON during daylight hours?
If automated panel, review for correct operating parameters
Office & Classroom | Location |  |  | Notes
Projectors
Computer & monitor
Task lighting
Local printer
Personal space heater
Personal humidifier
Personal air filter units
Personal coffee makers
Personal refrigerators
Other
Kitchen |  | Location |  | Notes
Kitchen Hood exhaust and make-up air units running?
Dishwasher exhaust fan running?
Commercial coffee maker still hot?
Walk-in cooler & freezer doors not completely closed?
Warming ovens still warm?
Opportunity to retrofit standing gas pilots to electronic spark?
Other |  | Location |  | Notes
Domestic Hot Water circulation pump running?
Domestic Hot Water temperature setting? (120° usually sufficient)
Thermal scan of building envlope. Look for heat signature from exterior doors and roof penetrations
Backdraft or isolation dampers not properly closing 100%?
Leaking or dripping valves or piping from DHW, Heating HW, & Chilled Water systems
Missing pipe insulation for DHW, Heating HW, Steam, & Chilled Water systems